OISD - 162

For Restricted

Circulation only

No.

SAFETY IN INSTALLATION

AND MAINTENANCE OF

LPG CYLINDERS MANIFOLD

# OISD-STANDARD-162

First Edition, July 1995

Oil Industry Safety Directorate

Government of India

Ministry of Petroleum & Natural Gas

OISD STANDARD-162

First Edition

July 1995

For Restricted

## Circulation only

No.

SAFETY IN INSTALLATION

AND MAINTENANCE OF

LPG CYLINDERS MANIFOLD

Prepared By

### COMMITTEE ON LPG CYLINDERS MANIFOLD

OIL INDUSTRY SAFETY DIRECTORATE

Government of India

Ministry of Petroleum & Natural Gas

2nd Floor, ‘Kailash ‘

26, Kasturba Gandhi Marg,

New Delhi - 110 001

NOTE

OISD (Oil Industry Safety Directorate) publications  are  prepared  for  use  in  the oil and  gas industry under Ministry of Petroleum and Natural Gas.   These are the  property of Ministry of Petroleum and Natural Gas  and shall not  be reproduced or copied and loaned  or  exhibited  to others without written consent from OISD.

Though  every  effort  has  been  made  to  assure  the accuracy and reliability of the data contained in  these documents, OISD hereby expressly disclaims any liability or  responsibility  for loss or damage resulting from their use.

These  documents are intended to supplement rather than  replace  the prevailing statutory requirements.

FOREWORD

Oil Industry in India is more than 100 years old. Over the years a variety of practices have been in vogue because of collaboration/association with different foreign companies and governments. Standardisation in design, operating and maintenance practices was hardly in existence at a national level. This lack of uniformity, coupled with feed back from some serious accidents that occurred in the recent past in India and abroad, emphasised the need for the industry to review the existing state of art in designing, operating and maintaining oil and gas installations.

With this in view, the Ministry of Petroleum & Natural Gas in 1986 constituted a Safety Council assisted by the Oil Industry Safety Directorate (OISD) staffed from within the industry in formulating and implementing a series of self regulatory measures aimed at removing obsolescence, standardising and upgrading the existing standards to ensure safer operations. Accordingly, OISD constituted a number of functional committees comprising of experts nominated from the industry to draw up standards and guidelines on various subjects.

The present document on ‘Safety in installation and maintenance of LPG cylinders manifold’ was prepared by the functional committee on LPG Cylinders Manifold. This document was prepared based on the accumulated knowledge and experience of industry members and the various national and international codes and practices.

This document will be reviewed periodically for improvements based on the new experiences and better understanding.

Suggestions from industry members/users may be addressed to :

The Coordinator

Committee on

LPG Cylinders Manifold

Oil Industry Safety Directorate,

2nd Floor ‘Kailash’

26, Kasturba Gandhi Marg,

New Delhi - 110 001

COMMITTEE

ON

LPG CYLINDERS MANIFOLD

Members							  Representing

SHRI A.K. VATTS	                                                   INDIAN OIL CORPN. LTD.		(LEADER)						(MARKETING DIVISION)

SHRI K.V. APTE					HINDUSTAN PETROLEUM

CORPN. LTD. (MARKETING)

SHRI S. ELANGO					BHARAT PETROLEUM

CORPN. LTD. (MARKETING)

SHRI S.C. GUPTA					OIL INDUSTRY SAFETY		(CO-ORDINATOR)					DIRECTORATE

--------------------------------------------------------------------------------------------------------------------------------------

In  addition  to the above, several other  experts  from  industry contributed  in the preparation, review and finalisation of  this document.

SAFETY IN

INSTALLATION AND  MAINTENANCE

OF LPG CYLINDERS MANIFOLD

CONTENTS

--------------------------------------------------------------------------------------------------------------------------------------

SECTION

--------------------------------------------------------------------------------------------------------------------------------------

1.0	INTRODUCTION

2.0	SCOPE

3.0	LAYOUT

4.0	DESIGN CRITERIA OF INSTALLATION

5.0	SPECIFICATIONS FOR EQUIPMENTS, APPLIANCES &

ACCESSORIES

6.0	INSTALLATION OF PIPING AND VALVES

7.0	PRE-COMMISSIONING CHECKS

8.0	MAINTENANCE OF CYLINDERS MANIFOLD

9.0	SAFE OPERATING PRACTICES AND LEAK TESTING

ANNEXURES

--------------------------------------------------------------------------------------------------------------------------------------

SAFETY IN  INSTALLATION  AND  MAINTENANCE

OF LPG CYLINDERS MANIFOLD

1.0	INTRODUCTION

There  are a number of LPG cylinders manifolded  installations existing in Hotels, Hospitals, Nursing Homes etc. Apart from a  BIS code, there is no detailed code which can  be  followed by the Oil  Industry  (through  their approved contractors). In view of the potential hazards of  such manifold installations, the need was  felt  to develop a standard code of practice in addition  to BIS  code  IS:6044 (Part I)-1971.  In the  Liquefied  Petroleum  Gas trade, commercial/Industrial cylinders   installations relate to the larger  type  catering/production arrangements such as Restaurants and Canteens located in  Hotels,  Hospitals, Nursing  Homes  and  Industrial Establishments such as Textiles, Baking, Glass  factory  etc.

2.0	SCOPE

This Standard :

-	Covers LPG cylinders (all types approved by CCE)  connected through  a manifold to commercial/ domestic,  industrial  burners where  the end use of LPG is for Commercial cooking/  production/ Laboratory purposes.

-	Supplements  IS:6044  (part I) - 1971  on  guidelines  for packed cylinder installation. Items covered under IS:6044 (part I) - 1971 are not being repeated and this standard may be referred in conjunction with IS: 6044 (Part I) - 1971.

-	Relates to safe practices in Design, erection, commissioning and  maintenance  of manifold  installations.  However,  detailed operational  practices  like handling emergencies  etc.  are  not covered.

Oil   industry  is  in  the  process  of  drawing  out   detailed specifications  of  the  equipments used in  the  manifolded  LPG cylinders   installations.   All   equipments   used   in   these installations shall meet the above specifications.

For  replacement schedules in the installation, equipment  guidelines suggested by the manufacturers may be followed.

3.0	LAYOUT

3.1  	General  guidelines for manifolded LPG cylinders  shall  be followed  from IS : 6044 (Part I) - 1971.  The additional  safety measures need to be taken are as under:

3.2	The  site for LPG cylinder manifold shall be  located  away from the kitchen.  Installation shall be slightly raised from the ground  level. Cylinders shall not be  installed  below  ground level  in cellars or basement. The cylinders shall be  stored  in dry, cool and well ventilated room.

3.3	Cylinders installation should not be located close to  steam pipes and boilers etc. to prevent cylinders from getting affected due to radiant heat.

3.4	Cylinders shall not be installed at a place where  they  are likely  to  cause  obstruction, suffer damage or  be  exposed  to conditions likely to affect safety.

3.5	The  cylinder  storage room shall be of  fire  -  resistant construction. Flammable materials like wood and plastic shall not be used.

3.6	Cylinders shall be located on a concrete or brick floor  in case of outdoor installation. The cylinder shall be installed  in upright position with the valve pointing upwards.

3.7	Since LPG is heavier than air, ventilation shall be provided at  floor  level  open to atmosphere. The  ventilators  shall  be provided with 2 layers copper or non - corroding metal wire  mesh not less than 11 to the linear centimeter.

3.8	Safety cap should be put on the cylinders which are empty.

3.9	The doors of the room where cylinders are  installed  shall open outwards.

3.10	Main  shut-off valve (Plug or ball-type)  on  the  pipeline emerging out of cylinder storage room shall be located in such  a manner  that it just falls outside the storage room and shall  be easily  accessible at all  times. At the point of entry  of  each work place, the line shall have a quick shut off valve  (plug  or ball-type).

3.11	The main shut - off and quick shut-off valves are  required in case the distance between the storage room and the work  place is more than 10 mtrs.

3.12	As  per  Statutory requirements  no  explosive  license  is required  for  multi cylinder installations.  However,  consumers having  unconnected filled cylinders with more than 100  kgs.  LPG shall obtain explosives license under Gas Cylinders Rules 1981.

3.13	The safety distance of packed installation shall conform  to Rule 3.1.6. of IS:6044 (Part I) - 1971.

3.14	Wherever  the pipelines are passing through  walls,  slacks shall be provided so that the pipeline does not get abraized.

3.15	The storage room shall have caution signs such as  “DANGER”, “HIGHLY  INFLAMMABLE  GAS  SHED”. “NO SMOKING”  etc.  painted  in luminous red paint outside at a prominent place.

3.16	A  minimum distance of 1 mt. shall be maintained between  the cylinder installation and the surface water drain, if any.

4.0	DESIGN CRITERIA OF 	INSTALLATION

4.1	In  order  to meet the  larger  requirement  of  commercial customers  it is necessary to connect a number of cylinders to  a manifold  so  that  the required quantity  of  gas  at  requisite pressure can be obtained.  The multi cylinder installations shall be designed as per IS:6044 (part I) - 1971.

4.1.1	It is required to visit the customer’s premises and select a suitable  site  for  cylinder  storage room  as per the  layout considerations.  In order to ascertain the requirement  complete details  shall be collected and noted in the format as  given  in annexure - I.

4.2	Requirement of Cylinder Bank/Burners :

Multi-  cylinder manifolds are mainly designed and used  for cooking  purpose.  The LPG requirement of customers  desirous  of converting  from other fuels to LPG can be assessed based on  the quantity of fuel used, its calorific values and heat transferring efficiency.

4.2.1	In the case of absolutely new installations the requirement may  be assessed alternatively by taking normal  consumption  per person  per day from 0.1 to 0.13 kg. depending upon the  climatic conditions. For existing as well as the new customers the no.  of cylinders required to be in use may be assessed after taking into account the burner consumption rate of LPG, % utilization  during the usage and the natural vapourisation capacity per cylinder.

4.2.2	Provision should also be made for 100% spare  capacity for cylinders as calculated above.

4.2.3	While deciding at the size of the manifold  it  should preferably be designed for higher no. of cylinders to  accommodate for increase in consumption in future.

4.2.4	Size of the cylinder storage room shall depend upon the number  of  installed cylinders designed for the  layout  of  the manifold (parallel or linear) and the cylinder arrangement in the storage  room  (Standard  or staggered).  Enough  room  shall  be provided for easy access to each and every cylinder.

4.3	CONNECTION CRITERIA OF LPG     CYLINDERS TO MANIFOLD :

4.3.1	All  The  cylinders at the  customers’  premises  shall always  be  connected  to the  manifold  wherever  the  installed cylinders  at  the  premises are more than  four.  The  cylinders should not be left unconnected or stored elsewhere.  Should there be  requirement  of  additional cylinders which are  to  be  kept loose,  the  customer  can  store  them  within  stipulations  as provided  for  in  Gas  Cylinders  Rules,  1981.  However    such cylinders  should not be stored in manifolded room. Each  arm  of the  manifold  shall  have a control valve. To each  arm  of  the cylinder  manifold,  cylinders  shall  be  connected  through   a pigtail.  For ‘SC’ type valve cylinders it is necessary to use  an adaptor to connect the cylinder pigtail. The distance between the nipples  on the manifold to which pigtails are attached,  depends upon the type of cylinder arrangement required i.e., standard  or staggered.   The  staggered  arrangement  is  to  be  used   when availability of space is limited.

4.3.2	The flexible hose/pigtail shall be in the same room and its length shall not exceed 2 M. Flexible hose/ pigtail shall not pass  through  doors, windows, walls, ceiling  (or)  floors.  The pigtails shall be accessible for inspection.

4.4 LOCATION FOR MANIFOLDED       INSTALLATIONS:

4.4.1	Manifolded installations upto 40 kgs LPG can be installed on any floor. Minimum floor area required 5M 2.

4.4.2	Manifold installations not exceeding 40 kgs. of LPG may be  installed  in doors on any floor within  the  same  workspace provided  the minimum distance between two such installations  is 3 M. The floor area for each installation should be at least 5M 2 and the aggregate quantity of LPG in all such installations  does not exceed 200 kgs.

4.4.3	Manifolded installations not exceeding 80 kgs. of LPG may be installed indoors on any floor provided the floor area is  not less than 12 M2 for such installation.

4.4.4	Manifolded installation not exceeding 80 kgs. of LPG  may be  installed  indoors  on any floor area  provided  the  minimum distance between the installations is 3 M, the proportion of such installations to floor area is one installation per 12 M2 and the aggregate  quantity  of LPG in all such  installations  does  not exceed 200 kgs.

4.5	As per IS:6044 (Part I) - 1971, small manifold (i.e.  Total capacity  upto 320 kgs) can be accommodated within the  building. For  bigger manifold (i.e. capacity 321 to 1000 kgs)  a  separate shed  away from the main building shall be provided keeping  adequate safety distances. For manifold capacity requirement of more than  1000  kgs, separate installations each not  exceeding  1000 kgs. shall be provided.

4.6	The manifold (header) pipeline shall not have any joints  to extend its length.

5.0	SPECIFICATIONS FOR 	EQUIPMENTS, APPLIANCES 	AND 	ACCESSORIES

5.1	GENERAL :

5.1.1	For   safe   efficient   performance   of   any   LPG  installation,  all equipments, appliances and  accessories  shall conform  to  the  laid down  standards  and  specifications.  For quality control more and more items are being covered by BIS.  In case  of BIS covered items, items approved by BIS only  shall  be used. In case any component is not covered by BIS Standard,  then the same shall have Oil Industry’s approval.

5.1.2	A  list  of such approved  manufacturers  for  various components can be had from the concerned oil company.

5.1.3	Major  components  of  LPG  installation  are  briefly described below:

5.2	PRESSURE REGULATORS :

5.2.1	Pressure Regulators are  devices used to regulate  the delivery pressure to the appliances for safe operation.  Adequate attention should be given to the Pressure Regulator selection and it must be chosen with due care. It shall have sufficient capacity  to  handle the volume of the gas required to  supply  maximum demand.   The  different types of pressure  regulators  presently available are :

-     low pressure regulators with high volume.

-    high pressure  regulators  with   fixed

outlet  pressure.

-   high pressure regulators with variable outlet

pressures.

5.2.2	All  high  pressure  regulators  to  be  used  in  LPG installations  shall  be  of approved  type.  Only  oil  industry approved high pressure regulators shall be used.

5.2.3	If the regulator selection is not proper the  appliance performance  will be affected by pressure fluctuations  and  will induce a slow pulsation in line pressure causing appliance  flame to vary.

5.3	GAS PIPES :

5.3.1	Copper, steel and mild steel tubes to be used  in  LPG service shall be as specified in IS:6044 (Part I) - 1971.

5.3.2	Steel  pipes, cold steel drawn  seamless  or  electric resistance welded (ERW) conforming to IS:3601 shall only be used.

5.3.3	Copper tubes shall be solid drawn with outside diameter of 10, 12, 20 mm as suitable conforming to IS:2501.

5.4	VALVES :

5.4.1	The following types of valves are normally used in  the LPG installations:

i)	Needle control valves

ii)	Fire control valves

iii)	Quick shut-off valves

iv)	Main shut-off valves

5.4.2	The valves designed to work on LPG shall only be  used. Materials  used  in these valves should not be affected  by  LPG. Type  of  valves to be used on LPG service should  be  of  proper pressure rating and meet oil industry specifications since BIS or equivalent standards are presently not available.

5.4.3	Cast iron and aluminum valves shall not be used.

5.5	BURNERS :

5.5.1	The burners used in commercial installations are  normally high pressure burners. These burners work at a pressure  of 0.315 kg/cm2 (4.5 PSIG) and above. Of the various models currently  in  use, from types which find the maximum  applications  are outlined below:

5.5.2	T-TYPE BURNERS OR

TORCH BURNERS

These  give a concentrated flame and are good for  water  heating and deep frying. The vessels used in this type of burners  should preferably have concave bottom.

5.5.3	These are vertical burners and height can be varied.

5.5.4	There are mainly two sizes in this type of burners i.e. T22 and T35 with consumption of 1 kg/hr and 1.6 kg/hr LPG  respectively. These burners are also called as T1 and T2.   Higher capacity burners are also available.

There are no BIS specifications so far. Hence oil  industry approved make shall only be used.

5.5.5	‘M’ TYPE BURNERS

These  have  a  spreading ring flame profile  and  are  good  for cooking  purpose.  These  burners are referred  to  as  ‘M’  type burners.

There are no BIS specifications so far. Hence, Oil  industry approved make shall only be used.

5.5.6     ‘V’ RING OR ‘L’ BURNERS

These  are long burners used horizontally and named  ‘V’  burners due  to  their shape. These burners are used  for  heating  long, broad  containers mussel ovens etc. The burner flame impinges  on the bottom of the vessel or plate at an angle of 45 degrees.

The  burner  shall  be so chosen such that  the  flame  does  not enter beyond the circumference of bottom plate of vessel.

5.5.7     CANTEEN BURNERS

5.5.7.1	These  burners are low pressure appliances widely  used  in commercial  installations.  These  are similar  to  the  domestic burner but of larger size.

5.5.7.2	Canteen burners shall conform to IS:5517 - 1969.

5.5.7.3	High pressure canteen burners as may be required by end users can be custom - built and used.

The heat efficiency of all the burners mentioned above should  be a minimum of 40% when tests are conducted as per BIS Standard No. IS:5117-1969.

5.6  CYLINDERS MANIFOLD :

5.6.1	Cylinder manifold is very important because of the fact that it is subjected to full cylinder pressure at all times.  The fabrication/  welding  of  the manifold should  be  of  the  best available  quality.  All such manifolds shall be  designed  to  a pressure  equivalent  to the maximum possible  cylinder  pressure (assessed at 65 degree C) of LPG i.e. at 16.87 kgf/cm2. The  test pressure should be 1.5 times the maximum pressure (assessed at 65 degree C) i.e. 25.35 kgf/cm2.

5.6.2	The  control valve (‘F’ type ) used  in  the  cylinder manifold arm shall be of the type used for LPG cylinders.  Valves manufactured  by  approved valve manufacturers  of  oil  industry shall only be used in manifold.

5.6.3	All joints in the manifold should be welded (except for valve fixation) and be easily accessible for inspection/  repairs etc.

5.6.4	Each manifold arm shall be fabricated out of a  single length of pipe. Joints to lengthen the arm, are not permitted.

5.7	CYLINDER PIGTAILS :

Normally  copper  pigtails are used to connect cylinders  to  the manifold.   However, flexible reinforced synthetic  rubber  pipes are  also  being used.  The quality of braided  synthetic  rubber tubes  shall  be  such  that it is least  affected  by  LPG.  The reinforcement i.e. braiding should be able to withstand the  same pressure  as  that  of  cylinder manifold. The  design  and  test criteria  shall  be  same  as that  of  cylinder  manifold.  Test pressure shall not be less than 25.35 /cm2. The free nut at  the end shall be of noncorrosive metal.

5.8	ADAPTOR :

This  device  is  used to connect the pigtails  to  the  cylinder valves  (self-closing) of the LPG cylinders. This  device  shall have  non-return device and shall have prior approval of the  oil industry.

5.9	NEEDLE CONTROL VALVE :

These  are  normally  used  to control the flow  of  gas  to  the burners. These valves should be of approved type of oil industry.

5.10	PRESSURE GAUGE :

A  good quality pressure gauge with a range of 0-3 kgf/cm2  (0-40 PSI)  shall  be provided in the pipeline after  the  first  stage pressure  regulator. The joint at which pressure gauge  is  fixed shall be thoroughly checked for leakage. Similar type of pressure gauges shall be provided in the pipelines after II stage  regulation.

5.11	EXCESS FLOW VALVE :

The excess flow check valve shall be provided on each arm of  the manifold  to  ensure stoppage of LPG supplies in  case  of  heavy leakage/damage to the pipeline in the downstream facilities.  The capacity  of  the excess flow valve shall be 50%  more  than  the maximum designed flow rate required through the manifold.

5.12	PIPING TUBING AND FITTINGS :

Proper  record of suppliers of equipments, its  installation  and Standard used shall be maintained.

6.0	INSTALLATION OF PIPING AND APPLIANCES

6.1	In  fabrication of LPG installation general guidelines shall be drawn from code of practice for LPG storage  installation IS : 6044 (Part I)-1971.

6.2	Those responsible for the installation of LPG equipment  and piping  etc. should understand the characteristics  of  LPG very  clearly  and  shall be  trained  in  proper  handling, installing and maintaining installations.

6.3	Detailed  drawings  giving specifications of  the  equipment used and layout of the entire installation must be  approved by concerned Oil Co. before undertaking work.

6.4	The route of pipeline which is spelt out very clearly in the approved  drawing, shall not deviate while laying  down  the pipelines. If need be the original drawings  can  be  got revised duly approved by Oil Cos.

6.5	All  pipelines  must  be either welded or brazed  so  as  to ensure that no leakage can take place even at pressures much higher  than  the working pressures.  Use of  threading  and jointing the pipeline through jointing compound shall not be resorted to.

6.6	The welding/brazing of the pipeline joints shall be done  by a trained and qualified welder.

6.7	If  the pipeline diameter is more than 50 mm, it  should  be welded and/or flanged. Smaller diameter  pipelines should only be welded/brazed.

6.8  The piping joints shall not be placed embedded in floors in inaccessible places. Wherever it cannot be helped, welding and  prior  pressure  testing of  pipeline  shall  be  done. Wherever the pipes are buried they shall not have any flange joints in the buried portion.

6.9	Joints  other than welded, if any, are to be so placed  that they shall be readily accessible, so that leakage tests  can be conducted without any difficulty.

6.10	Piping  both  embedded in floor and above  ground  shall  be protected against physical damage and corrosion. These shall be  covered  with bituminous wrap coating at the buried portion for LPG.

6.11	Cast iron and aluminum pipe fittings shall not be used.

6.12	All  materials  including  non-metallic  parts  for  valves, seals,  gaskets  and diaphragms shall be  resistant  to  the action of the LPG under the service conditions to which they are subjected.

6.13	Plugs shall be solid steel plugs or steel ball plugs.   Cast iron or brass plugs shall not be used.

6.14	Copper  or brass pipe or tubing shall be seamless and  shall only be used. for sizes 12.5 mm and under.

6.15	The  pipeline  connecting  the  storage  shed  to  the  main installation  should preferably be brought overhead  without creating any hazard for the people/vehicles passing  through the  same.  In case of any foreseen hazard the pipeline can be laid embedded in the ground.

6.16 	Quick shut-off valves designed to work on LPG, shall only be used  for  mainline for shut-off operations.   The  jointing compound shall be of Industry approved type.

6.17 	No  heating  devices  of  any nature  are  permitted  to  be installed in the storage shed. Similarly,  pipelines location shall be such so as to  avoid any over heating/cooling at any length of the pipeline.

6.18	The  single stage pipeline network (down the range of  first stage  pressure  regulator)  from the  storage  shed  onward should  work at pressure very close to the working  pressure of the appliances.  Under no circumstances, the pressure  of the pipelines should exceed 22 PSI (1.5 kg/cm2). This should  be obtained by double stage regulation of  pressure, if  necessary. A typical layout of installation is given in Annexure III.

6.19	Water spray of 10 liters PM/M2 on  LPG  manifold (with connected LPG cylinders) may be considered depending on installation size.

6.20	Whenever cylinders are taken out of manifold  after closing the  isolating valve, the idle ends of adaptor end shall be plugged  with dummy valves (if new cylinders are not  fixed) to avoid leakage from adaptor end to atmosphere.

7.0	PRE-COMMISSIONING CHECKS

7.1	Every multi-cylinder installation essentially consists of the following:

1.	Cylinders

2.	Manifold

3.	Valves

4.	Pigtails

5.	Regulators

6.	Burners

It shall be ensured that all the above equipments conforms to  a approved layout drawing and other specifications as mentioned in the foregoing sections.

8.0	MAINTENANCE OF CYLINDErs MANIFOLD

Maintenance of the cylinders manifold and the equipments shall be undertaken regularly and the periodicity of the maintenance shall be as under:

8.1	PERIODICITY :

i)	Valves : All the valves i.e. needle valves, manifold control valves emergency valve shall be checked once  in a year.

ii)	Piping  and  manifold:  It should be checked  once  a  year visually.  pneumatic   testing   of pipe lines once in 5 years.

iii)	HP  & LP Regulators once a year for its accurate  throttled pressure.

iv)	The burners shall be regularly cleaned.

v)	Pigtails  shall  be  checked  every time empty cylinder is replaced  by a filled cylinder and replaced in case of any physical damage.

8.2  INSPECTING AUTHORITY :

1)	All  the  manifold  installations  shall be checked once in six   months  by the dealers authorised mechanic and record maintained at the installation location.

2)	The installation shall be checked once in a year by the concerned  Oil company Sales Officer of the area or by  any authorised representatives of the Oil Co.

3)	Major installations  shall  also  be  inspected  by  Senior Officials of the Oil Co.  The  inspection  shall  be  carried out as  per  the  check  list attached.  (Annexure II)

9.0	SAFE OPERATING PRACTICES AND LEAK TESTING

9.1	All  the  safety  precautions outlined in the Gas Cylinder Rule  1981 shall be complied with.

9.1.1	Storage of Cylinders

i)	The  storage  of cylinders is governed by the  Gas Cylinders Rules - 1981 and the appropriate  safety distances as given in the rule should be  complied  with.

ii)	Cylinders shall be stored in a cool,  dry,  well ventilated place under cover,  away from  boilers  open flames,  steam pipes or any potential sources   of  heat and such place of storage shall be easily accessible.

iii)	The   storage   room   or  shed  shall be of fire resistant construction.

iv)	LPG filled cylinders must never  be  stacked  in horizontal position.

v)	Cylinders   containing   flammable   gases  shall  be  kept separated from each other  and  from  cylinders containing other  types  of  gases  by  an  adequate distance or by a suitable partition wall.

vi)	Cylinders shall not be stored  under  conditions which will cause them to corrode.

vii)	Cylinders  shall  not  be stored along with any  combustible material.

viii)	Unconnected cylinders shall be kept away from   the LPG cylinder manifold.

ix)	All electric meters, distribution boards, switches, fuses, plugs  and  sockets,  electric fixed lamps,  portable hand lamps and motors shall be of flame-proof construction.

9.1.2	Handling and Use

i)	Cylinders shall be adequately supported  during handling.

ii)	Trolleys and cradles of adequate strength shall as far as possible be used when moving the cylinders.

Use  of  high  powered  magnets  for  lifting  the                cylinders  and chains for slinging  the  cylinders                shall not be permitted.

Valve or any other fitting on the cylinder  should                not be lubricated.

iii)	The  cylinders shall be handled carefully and  not be allowed to fall upon one another or  otherwise                subjected to any undue shock.

iv)	Sliding, dropping  or playing  with  cylinders  is                prohibited.

v)	Liquefied Petroleum Gas cylinders shall always be kept in  an upright position and  shall be so placed that they cannot be knocked over.

vi)	Open flames,  lights,  lighting of fires,  welding                and smoking shall be prohibited in close proximity.

Cylinder  should  not be lifted with  magnets  and                chains should not be used for slinging.

9.2	LEAK TESTING:

9.2.1	Criteria For Leak Testing

i)   It  shall  be ensured that the manifold  provided  has  been subjected to  the  test  pressure of 25.35 kgf/cm2 (360 psig) at  least for a minimum  period  of  1  hour  inspected by the Oil Industry approved contractor.

ii)	It shall be ensured that the fire  extinguisher  and  sand buckets  are  provided  and  installations  are   adequately protected from weather conditions.

9.2.2	Detection of Gas Leakages

Gas leakage can be easily detected by its                characteristic smell and more positively located                by means of a soap solution.

9.2.3	For  pinpointing the source of leakage  only  soap solution shall be used.   A NAKED FLAME MUST NEVER BE  USED  because  there  is  risk of causing fire accident.

9.2.4	Source of Leakages

A.   Cylinders :

I)         Welded  seams

ii)	The cylinder/valve connection bung joint.

iii)	Cylinder valve

B.	Check leakage from Pressure 	Regulator at :

i)	Near the joints.

ii)	In the pressure regulator itself.

iii)	Check leakage from the piping and manifold

Regulator and the appliance inlet nozzle.

iv)	Check leakage from cooking 	appliances at

i.) All threaded connections.

ii.) The appliances itself.

9.3	ACTION TO BE TAKEN WHEN LEAKAGE IS DETECTED

i)	Leakage of cylinder: Any cylinder which develops a leak  should  be promptly removed to  an  isolated open place away from any source of ignition.

ii)	In  case  of  leakages of  piping,  appliances  or   pressure regulators, close the valves and isolate the part, disconnect the cylinders and place  the safety cap on the valve of the cylinder. NEVER repair the appliance or any other part of system when in use.

ANNEXURE-I

COMMERCIAL CYLINDER INSTALLATION ASSESSMENT FORM

Name of the customer	:

Address	:

Category	:	Hotel/School/Hospital/			Laboratory/Other/College 			(Specify) /Mess

Type of Hotel:	5*    4*    3*    2*    Other (Specify)

Type	:	New Hotel/unit

: Existing unit using other fuels converting to LPG

: Existing unit using LPG and requires enhancement

Adequate space available for

cylinder storage 	:	Yes/No

Type of Food prepared/quantity	:

No. of Meals per day:

No. of cups of Coffee/Tea per day:

Snacks and other preparations per day:

Sweets preparation per day:

Timing	:	Duration (No. of hrs)

Coffee/Tea

Snacks

Sweets

Meals

Other fuels used per day/week :

|  | Weight in Kgs. | Calorific Value |  | Total heat output | Heat Transfer efficiency | Requir-ement of LPG in Kgs. |
| --- | --- | --- | --- | --- | --- | --- |
| Firewood |  |  |  |  |  |  |
| Charcoal |  |  |  |  |  |  |
| Kerosene |  |  |  |  |  |  |
| Coal |  |  |  |  |  |  |

No. of cylinders required per month :

(Approximate to nearest higher round number)

Burner requirement:

Type of	 Consumption  No. of      Total

Burner	 per hour        Burners    Consumption

per hour

T 22

T 35

M 22

M 35

V 300/600/900

Canteen burner

M 100/140

Usage:

Intermittent	:

Continuous	:

No. of installed cylinders for above requirement (Approximate to next higher figure):

Total installed cylinders :

Signature of Inspecting Officer

Name :

Designation :

Date :

ANNEXURE - II

LOCATION

MULTI CYLINDER INSTALLATION INSPECTION

Date of Last

Consumer No._______	Inspection  _______

Address:____________________________________________________________________________________________________________________________________________

Phone   No.__________________________

End  Use____________________________

Name of Dealer_______________________

Address  _____________________________

_____________________________________

_____________________________________

Others _______________________________

Phone No.__________________________

Installation Supplied By:______________

Type of Establishment	: Hotel Industry

Laboratory :	Hospital/Nursing Home

Educational  Institution__________________

Others Specify_________________________

Sanctioned Qty:________________________

Period_______________________________

VideletterNo.__________________________

1.Cylinder Location :

a. Installed Indoors	                     Yes/No

b. If so, Floor area as per  norms       Yes/No

c.  Adequate ventilation at low level

to directly outside air provided	      Yes/No

d.  Minimum distance of 3m is	      Yes/No

maintained between installation

and any building, public place,

roadway and other surroundings

provided			      Yes/No

e. Installation is protected from

excessive weathering from sun,

rain etc.			      Yes/No

2. Position of Cylinder to facilitate

a.    Changing and quick removal   Yes/No

b.    Access to connection and

regulating device	                     Yes/No

c.     Operation of cylinder valves    Yes/No

d.     Cylinder installed upright        Yes/No

e.     Cylinder installed on grounund

level			        Yes/No

f. Cylinder are not installed where

they may get over heated

(3m away) (Close to steam

(Close to steam pipe, boilers

open flame etc.,		    Yes/No

g. Cylinders are not causing

an obstruction		    Yes/No

h. Cylinder raised in case of

outdoor installation (on a

concrete or brick floor)           Yes/No

i.Cylinders are 1m away from

entrances of openings (from

culverts, depressions, opening

leading to below ground level

compartments and drains) 	Yes/No

j.  Smoking is completely forbidden

within 3m  while connecting

and disconnecting	                  Yes/No

k.  If mounted on trolley, the

trolley is stable 		     Yes/No

3.	Cylinders Manifold :

a. All joints between manifold

header and cylinder connection

are readily accessible 	     Yes/No

b. All  materials, fittings etc. used

in cylinder manifold comply

with BIS stipulation.	     Yes/No

c. In case of pressure regulator

and automatic change over

device connected by semi

flexible connectors and are

rigidly  supported.	                  Yes/No

4.     Pressure Regulators :

a. PR comply BIS stipulation

(IS:4786-1968)		     Yes/No

b.  PR fitted with a relief valve and

positioned to avoid

hazards 		     Yes/No

c.	PR and other control devices

adequately supported	     Yes/No

d.	PR manufactured by_____________

5.	Piping, Tubing and Fittings :

a.	All piping, tubing and fittings

comply BIS  stipulation      Yes/No

(IS:2501-1963 - Copper

Tubes)

(IS:3601-1966 - Steel

Tubes)

(IS:1239 - Part I) - 1968

mild steel tubes)

6.	Flexible Hose/Piping :

a.	Cylinder and the appliances

are in same room	Yes/No

b.	Length of hose does

not  exceed 2 m             Yes/No.

c.	Appliance connected

portable		Yes/No

d.	Accessible for

inspection		Yes/No

e.	Not twisted - looped or

kinked			Yes/No

f.	Joints are accessible for

inspection		Yes/No

g.	Piping and electric wiring

are at	least 60 mm

away and is fixed below

electric wiring		Yes/No

7.	Leak Testing :

a.	Naked flames are not used

for checking gas tightness

of the installation            Yes/No

b.	Soap solution is used to

detect	leak		 Yes/No

c.	Defective pipes or fittings

replaced and not

repaired		 Yes/No

d.	Consumer knows the action

to be taken in case of

leakage		 Yes/No

e.	Consumer knows the

action to be taken in case

of fire			 Yes/No

f.	Consumer knows the

action to be taken in case

of damage to or failure

of any part of installationYes/No

Action to be taken:

Inspection Officer Signature ______________________________

Regional Office ________________________________________

Annexure -III

LPG CYLINDERS MANIFOLD INSTALLATION